Title: **Stop/Start/HOA of a Three-Phase Motor Circuit** Job: 26

Course: Introduction to Automation Unit: Introduction of PLC CLO: 2, 4

Name \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Station \_\_\_\_\_\_\_ Date \_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Objectives**

1. Student shall reinforce their knowledge of a stop/start motor control circuit.
2. Student shall develop a knowledge of hand-off-auto circuits and their use.
3. Student shall apply this circuit in a three-phase motor control scenario.

**Assessment**

Students shall demonstrate a comprehension of the objectives listed above by scoring a minimum of 75% on this shop job. Grading shall be based on the Introduction to PLC rubric.

**Instructions**

Design a stop/start motor control circuit using two sets of momentary pushbuttons. The circuit will also utilize a hand-off-auto (HOA) selector switch to select modes and one ESTOP on the manual motor control (MMC) circuit. Whenever the HOA switch is in the “hand” position, the circuit will operate without the use of the PLC. Whenever the HOA switch is in the “auto” position, the circuit will operate through the PLC. Each mode, hand, for MMC, and auto, for PLC, shall have their own stop and start pushbuttons and green, red and yellow lights. Whenever the motor is running, both green lights shall come on and both red lights shall be off. When the motor is not running, both green lights shall be off and both red lights shall be on. Whenever an overload occurs, both yellow lights shall illuminate. If an overload occurs, both circuits shall de-energize the control circuit. If the ESTOP is pressed, both circuits shall de-energize the motor as well. When the circuit is placed in “hand” the blue light on the PLC panel shall illuminate. Use the space on the opposite side of this page to design the manual motor control circuit and PLC program. Once complete, review the design with the instructor. After obtaining approval, configure the program in RSLogix 500. Have the instructor review the program before downloading. Once the program has been reviewed, verify and download the program.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Input | Description | Output | Desc | Three-Phase Motor Starters | | |
| I/0 | ESTOP | O/0 | Green | L1 | NO -| |- |  |
| I/1 | MS Aux NO Contacts | O/1 | Yellow | L2 | NO -| |- | T2 |
| I/2 | HOA Auto Input | O/2 | Red | L3 | NO -| |- | T3 |
| I/3 | Overload NO Contacts | O/3 | Blue | 13 | NO -| |- | 14 |
| I/4 | PB1, NC | O/4 | MS Coil | Auxiliary Contacts | | |
| I/5 | PB2, NO | O/5 |  | 23 | NO -| |- | 24 |
| I/6 |  |  |  | 31 | NC -|/|- | 32 |
| I/7 |  |  |  | Overload | | |
| I/8 |  |  |  | 95 | NC -|/|- | 96 |
| I/9 |  |  |  | 97 | NO -| |- | 98 |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |
| --- | --- |
|  |  |
|  |  |
|  |  |
|  |  |
|  |  |
|  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Discussed design \_\_\_\_\_\_\_, Test logic without motor \_\_\_\_\_\_\_, With motor \_\_\_\_\_\_\_



